## Grid-Tied Array Sizing
Grid-Tied Array Sizing
Yearly average energy consumption = |  | kWh, ÷ 365 days = |  | kWh/day
Desired kWh per day from solar (Decimal equivalent) =
kWh/Day X | Desired kWh from Solar = | PV System Kwh/day
PV system kWh/Day =
Average Peak sun/hours per day for location=
Temperature difference correction factor (TDC) =
DC to AC combined correction factor (DCACCC)
Chosen PV module=
STC Watt Rating= |  | Watts
PV system kWh/day ÷ | Avg Peak Sun Hours/Day ÷ | TDC ÷ | DCACCCC X | 1000= | Required PV array watts
Required PV Array Watts ÷ | Module STC Watt Rating = | Total Modules Required

## Correction Factors
Temperature Difference Correction Factor
Based on a typical performance loss of 0.5% per degree ⷪC in PV modules that results from increased temperature, calculate the TDC by:
· Determining the anticipated module temperature
· Determining the temperature difference between your value and the STC value of 25ⷪ C
· Multiply the resulting temperature difference by 0.5% ti find the percentage of loss
Example 40ⷪ C projected module temperature - 25ⷪ C STC value = 15ⷪ C x 0.5% = 7.5% loss, converted to a decimal multiplier = 0.925 multiplier
DC-TO AC Combined Correction Factor
Component Correction Factors | Default | Chosen Value | Range
PV Module Nameplate DC rating | 0.95 |  | 0.80-1.05
Inverter and Transformer | 0.92 |  | 0.88-0.98
Mismatch | 0.98 |  | 0.97-0.995
Diodes and connections | 0.995 |  | 0.99-0.997
DC wiring | 0.98 |  | 0.97-0.99
AC wiring | 0.99 |  | 0.98-0.993
Soiling | 0.95 |  | 0.30-0.995
System Availability | 0.98 |  | 0.00-0.995
Shading | 1 |  | 0.00-1.00
Sun-Tracking | 1 |  | 0.95-11.00
Age | 1 |  | 0.70-1.00
Product of chosen correction factors = 0.96001-0.09999
Choose a correction factor value for each line item, then multiply to determine the DC-to-AC combined correeection factor.
Using the default values as an example, the factor woruld be:
0.95X 0.92X 0.98X 0.995X 0.98X 0.99X 0.95X 0.98X 1.00X 1.00X 1.00= 0.77 DCACCC

## Grid-Tied Inverter Selection
Grid-Tied Inverter Selection
Number of PV Modules determined to be =
Chosen Module Wattage @ STC = |  | Watts
Number of PV Modules X | STC Wattage = | Maximum Wattage Inverter Throughput Required
Maximum Wattage Inverter Throughput Required ÷ | Number of Desired Inverters = | Maximum Wattage needed per Inverter
Number of PV modules ÷ | Number of Inverters = | Number of Modules per Inverter
Preferred inverter(s) make, model and basic Specifications:
Determine the number of modules required in series for the chosen inverter to operate comfortably within the DC input voltage range. This is done through review of the manufacturer's literature, or through the use of manufacturere-provided selection software. Ensure that the configuration of series-parallel modules in the array or subarrays, matches the inverter specifications appropriately. When mismatches exist, adjustments must be made in the inverter model chosed, the PV module wattage chosen or the number of modules in the array. For selection software use, the highest and lowest expected ambient temperatures for the region as wasll as the modules specifications will be needed.